A.  GENERAL

The following is the Asahi/America and Agru formal submittal for supplying High-Purity PVDF pipe, valves, and fittings.  The submittal is inclusive for all dimensions offered.

B.  PRODUCTS

1.  Resins

All pipe and fittings supplied will be made of Polyvinylidene Fluoride resin from one manufacturer, Solvay.  The resins is to be a high purity grade resin made utilizing the suspension process.  The following designates the resins to be supplied:

Pipe:		Solef 1010/0001-HP PVDF resin

MFI = 4 - 7 g/10 min.

Fittings:	Solef 1008/0001-HP PVDF resin

MFI = 22 - 27 g/10 min.

Solef resin is 100% PVDF with absolutely no antioxidants, anti-static agents, colorants, fillers, flame retardants, heat stabilizers, lubricants, plasticizers, preservatives, processing aids, U.V. stabilizers, or any other additives.  Solef PVDF also is FDA approved for contact with food under Title 2.1, Chapter 1, Part 177-2510 of the code of Federal Regulations.  Demonstrating that the resin is ideal for applications requiring minimal contaminants.  The Plastic Piping Institute (PPI) has listed Solef 1010 resin with the Hydrostatic Stress Design Board, the only PVDF resin to be listed with PPI.

The following chart provides data on the physical properties of the Solef PVDF 1000 resins.

Physical Properties

| Characteristic | Standard | Units | Value |
| --- | --- | --- | --- |
| Density | ASTM D 792 | g/cm3 | 1.78 |
| Tensile Stress | ASTM D 638 | PSI | 7,975 |
| Ultimate Tensile strength | ASTM D 638 | PSI | 6,960 |
| Elongation at break | ASTM D 638 | % | 50 |
| Flexural Strength | ASTM D 790 | PSI | 12,180 |
| E-modulus | ASTM D 790 | PSI | 435,000 |
| Impact Strength | ASTM D 256 | ft-lb./in | 2.80 |
| Shore -D hardness | ASTM D 2240 | ---- | 80 |
| Abrasion Resistance | DIN 53 754 | mg/100 cycle | 0.5 - 1 |
| Friction Coefficient | DIN 375 | ---- | 0.45 |
| Dynamic friction Coefficient | ---- | ---- | 0.34 |
| Crystalline melting point | DIN 53 736 | ( C ( F | 350 177 |
| Vicat Point | ASTM D 3418 | ( C ( F | 293 145 |
| Brittleness Temperature | ASTM D 746 | ( C ( F | -40 -40 |
| Thermal Conductance | ASTM D 177 | BTU-in/hr(ft((( F | 1.32 |
| Coefficient of thermal expansion | DIN 53 453 | ( R - 1 | 6.7x10-5 |
| Specific Volume Resistivity | ASTM D 257 | Ohm cm | 5 x 10 14 |
| Surface Resistivity | DIN 53 482 | Ohm | ( 10 13 |
| Dielectric Strength | ASTM D 149 | kv/mm | 40 |
| Burning rate | UL94 | ---- | V-0 |
| Limiting Oxygen index | ASTM D 2863 | % | 44 |

2.  Production

Pipe

All Pipe Supplied for High-Purity applications is produced on a dedicated extruder within an enclosed class 1000 cleanroom and packaged under class 100 Laminar flow filters within the cleanroom.  All pipe is stress-relieved on-line as it is extruded.

All pipe packaged  with PE film placed over the ends and then capped.  The entire pipe is inserted into a PE Sleeve and the ends are heat sealed.  The packaged pipe is finally placed within a hard PE tube and capped for protection during shipping.  The following chart designates quantities of pipe per PE shipping tube.

1/2”	   five per tube

3/4” 	   four per tube

1”	   three per tube

1 1/4”	   one per tube

1 1/2” 	   one per tube

2”	   one per tube

`				2 1/2”	   one per tube

3”	   one per tube

4”	   one per tube

6”	   one per tube

8”	   one per tube

10”	   one per tube

Fittings

Fittings supplied are molded in a dedicated molder class 100 Laminar flow filters above the resin intake.  After secondary machining fittings are passed through the precleaning process.  The cleaning is an automated process, passing each fitting through a series of six basins. The DI water specification is as follows:

T	=	70(C

TOC	<	10 ppb

R	=	18 meg. ohm

Each basin uses new hot DI water, there is not any recycled and each basin has an increase flowrate.

Each fitting is cleaned for 1 hour and all cleaning, drying and packaging is done in a class 100 cleanroom.  After the final rinse the PVDF components are dried with pure Nitrogen at 70(C.

Fittings are doubled bagged in clean PE/Nylon composite bags that are tear-proof.  Both bags are purged with clean dry Nitrogen to protect against moisture.

Surface roughness is continuously monitored during production to ensure all pipe and fittings meet the following requirements:

1/2” - 3”	Ra = 7.80”	(0.20m)

4”		Ra = 13.80”	(0.35m)

6” - 8”		Ra = 19.70”	(0.50m)

In addition, all HP pipes and fittings meet the Asahi/America specification for HP piping systems.

3.  Quality Control

Asahi/America, Inc. is capable of providing quality assurance certifications on all components based on lot numbers and manufacturing dates.  If certifications

are necessary notify Asahi/America at time of order, lot numbers are recorded on orders that are requested.  All certifications will be supplied by mail after material

has been shipped.

4.  Test Data

The test listed below are conducted on a regular schedule.  Dynamic leach out tests are done each time there is a resin change.  Static leach out tests are done

once per year.  The ESCA analysis is conducted a minimum of three times per year and after any production changes.

For the results of these please see appendix of submittal.

a.  Leach out data - Dynamic.

b.  Leah out data - Static

c.  ESCA Analysis   C:F< 87 pipe and fitting

5.  Product

A.  Dimensional Catalog

Enclosed is a copy for pipe and fittings.  The catalog includes dimensions on all pipe and fittings, both socket and butt-fusion.  Also enclosed is a listing of non-standard machine fittings available for special needs.

B.  Valves

All valves are to be supplied cleaned and lubricant free.  Valve Components will be DI rinsed for a minimum of a1/2 hour.  Valves shall be purged with Nitrogen and double bagged.

Diaphragm Valves: 1/2” - 2” shall be of a PVDF body with PTFE diaphragm.

Valves shall be designed with an adjustable travel stop and position indicator.

Valves shall be single body design with butt-fusion ends.

Diaphragm Valves: 2 1/2” - 8” shall be of a PVDF body with a PTFE diaphragm and shall have flanged ends.  All diaphragm valves will be provided with an adjustable travel stop and position indicator.

T-Diaphragm Valves: 3/4"-4" shall be a molded, single body zero dead leg design.  The valve shall be self draining in the horizontal position.  All valves are to be class 150, weir style PVDF body, PP bonnet and PTFE diaphragm with an EPDM backing.  All valves are to be butt-fusion ends.

Butterfly Valves:  All sizes 1-1/2” - 12” shall be a class 150 lug style PVC, PP or PVDF body.  Seat liner and seals shall be Viton or platinum chloride cured silicone.  Disc shall be PVDF as outlined above.  316 SS lugs mounted into the body are optional from the manufacturer.

Check Valves:  All sizes class 150, ball type PVDF body with Viton seat and seals.  230 PSI at 73.4(F for sizes 1/2” through 2-1/2” nominal PSI at 73.4(F for sizes above 2-1/2” nominal.

Enclosed are copies of necessary valve catalogs.  Valve catalogs include:

material of construction, pressure ratings and dimensional information.

C.  Pressure Ratings (pipe and fittings)

230 PSI at 68(F for sizes 1/2” - 2 1/2”

150 PSI at 68(F for sizes  3” - 12”

Option:  230 PSI at 68(F for sizes 3”-8”

Valve pressure ratings are based on the valve material and style.  See enclosed valve catalogs for ratings.

Pressure Rating

Correction Chart

| Temperature | Temperature | Correction |
| --- | --- | --- |
| ( F | ( C | Factor |
| 68 | 20 | 1.00 |
| 80 | 27 | 0.95 |
| 90 | 32 | 0.87 |
| 100 | 38 | 0.80 |
| 120 | 49 | 0.68 |
| 140 | 60 | 0.58 |
| 160 | 71 | 0.49 |
| 180 | 82 | 0.42 |
| 200 | 93 | 0.36 |
| 240 | 115 | 0.25 |
| 280 | 138 | 0.18 |

Multiply the nominal pressure rating of the pipe by the appropriate 			correction factor.  (Example: 2” line at 100(F : 230 PSI x 0.80 = 186 PSI)

D.  Hanging Criteria

It is recommended to hang all PVDF pipelines in a manner that prevents point loads.  Hangers that hold 360( around the pipe are recommended over a U-Bolt hanger.

Support Spacing Recommendation

| Nominal Size | 68( F 20( F | 86( F 30( F | 104( F 60( F | 122( F 50( F | 140( F 60( F | 158( F 70( F | 176( F 80( F |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2” | 3 | 2.5 | 2.5 | 2 | 2 | 2 | 2 |
| 3/4” | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2 |
| 1” | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 |
| 1 1/2” | 4 | 3.53 | 3 | 3 | 3 | 3 | 3 |
| 2” | 4.5 | 4 | 4 | 3.5 | 3 | 3 | 3 |
| 2 1/2” | 5 | 4.5 | 4 | 4 | 3.5 | 3 | 3 |
| 3” | 5.5 | 5 | 4 | 4 | 4 | 3.5 | 3.5 |
| 4” | 6 | 5 | 5 | 4 | 4 | 4 | 4 |
| 6” | 7 | 6 | 6 | 5 | 5 | 4.5 | 4.5 |
| 8” | 7.5 | 7 | 6 | 6 | 5.5 | 5 | 5 |
| 10” | 8.5 | 7.5 | 7 | 6.5 | 6 | 6 | 5.5 |
| 12” | 9.5 | 8.5 | 8 | 7 | 7 | 6.5 | 6 |

C.  Execution

1.  Material Storage

All high-purity components received for installation shall be kept in original shipping containers.  Receivers should verify the condition of the materials after shipment at this point.  Any discrepancies should be addressed with Asahi/America immediately.

Materials should then be stored in a sheltered location protected from sunlight and rain to prevent damage and contamination.

A.  Pipe should be stored horizontally in its original protective tubes.  Each tube will be labeled with its contents, therefore eliminating the need to open the tube until the material is to be fabricated.  Tubes should be supported every three feet or less.  Pipe should not be stacked more than three to four feet in height.  If multiple sizes are to be stored, the larger diameters should be placed on the bottom and lighter smaller diameters on the top.

B.  Fittings should be kept in original boxes with bubble wrap until ready for use.

Outer secondary protective bag should not be removed until just prior to cleanroom entrance.  Fittings with ripped outer bags should be rebagged immediately by wiping down inner bag and then resealing a new outer bag.  Torn inner bags should be set aside for recleaning of components.

2. Manufacturer Representation

On each pipe installation Asahi/America is committed to be on site at the time of job start-up to provide training on use of supplied welding equipment.  The time required for on-site supervision shall be negotiated during the bid process.  Any time beyond the negotiated amount will be billed to the contractor on a time and expense basis.  Asahi/America’s  extensive field representation through our distribution network and our field technicians can provide almost immediate field assistance for emergencies to reduced any down time.

Training will consist of Asahi/America personnel or a certified representative to fully educate installers on the welding tools.  Each welder will be required to demonstrate the full process of welding.  The process includes: set up of the tool, loading of the pipe and/or fittings, alignment of the tool, and the weld process.  Training will also include minor maintenance techniques to keep tools in ideal operating conditions.  After an operator has demonstrated his or her ability to operate the equipment, Asahi/America will issue a certified welders card for the equipment being used.  It is important that the factory certified all welders per job to avoid any misunderstandings.

3.  Recommended Welding

Technique-Butt, Socket, Tekweld,

Non-Contact

The following section outlines four welding methods available from Asahi/America.  Each method has its benefits for various applications.  In each case Asahi/America has the equipment and expertise to provide the welding method you demand.

A.  Conventional Butt-Fusion

All pipe , valve, and fitting joints are to be prepared using the butt-fusion technique as outlined in ASTM D-2657, Section 9.  The welding equipment is to be rented or purchased from Asahi/America.  Proper equipment selection should be based on pipe size and site conditions.  For assistance on tool selection, Asahi/America should be consulted.  For Butt-Fusion Asahi/America offers the following:

(  The 4” Proweld shop - for sizes 1/2” - 4”

(  The 6” Proweld shop - for sizes 1 1/2” - 6”

(  The 10” Proweld shop - for sizes 1 1/2” - 10”

(  The UF2000/1* - for sizes 1/2” - 2”

(  The UF2000/2* - for sizes 2 1/2” - 6”    (8” and 10” optional)

* UF tools provide stringent welding quality control.  They are designed for non-contact IR butt-fusion, but incorporate standard butt-fusion as an operating option.  Consult factory for availability.

The welding parameters for HP-PVDF piping assembled utilizing the butt-fusion procedure are located in the table below.

| Nominal Size | Pressure Rating (lb. force) | Initial Melt Pressure (lb. force) | Melt Pressure (lb. force) | Heat Soak Time (secs) | Change Over Time (secs) | Cool Down Time (min.) |
| --- | --- | --- | --- | --- | --- | --- |
| 1/2” | SP 230 | 3 | 1 | 25 | 3 | 3 |
| 3/4” | SP 230 | 4 | 1 | 25 | 3 | 3 |
| 1” | SP 230 | 7 | 1 | 30 | 3 | 3 |
| 1 1/4” | SP 230 | 8 | 1 | 35 | 4 | 4 |
| 1 1/2” | SP 230 | 12 | 2 | 40 | 4 | 5 |
| 2” | SP 230 | 16 | 2 | 45 | 4 | 5 |
| 2 1/2” | SP 230 | 16 | 3 | 50 | 4 | 5 |
| 3” | SP 150 SP 230 | 22 | 3 | 40 | 4 | 6 |
| 4” | SP 150 SP 230 | 34 | 4 | 50 | 4 | 7 |
| 6” | SP 150 SP 230 | 70 | 5 | 70 | 4 | 10 |
| 8” | SP150 SP 230 | 108 | 10 | 90 | 6 | 12 |
| 10” | SP 150 | 172 | 15 | 120 | 8 | 14 |
| 12” | SP 150 | 272 | 20 | 150 | 10 | 20 |

B.  Socket Fusion

All pipe , valves, and fittings are to be prepared using the socket-fusion technique as outlined in ASTM D-2657, Section 8.  The welding equipment is to be rented or purchased from Asahi/America.  Proper equipment selection should be based on pipe size and site conditions.  For assistance on tool selection, Asahi/America should be consulted.  For socket-fusion Asahi/America can offer the following equipment:

2” Hand Held Proweld Socket-Fusion Tool - for sizes 1/2” - 2”

4” Bench Socket-Fusion Tool - for sizes 3/4” - 4”

The welding parameters for HP-PVDF piping assembled using the socket-fusion method are in the table below.

| Size | Heat Soak Time | Adjust Time | Cooling Time |
| --- | --- | --- | --- |
| 1/2” | 3 | 3 | 3 |
| 3/4” | 4 | 3 | 3 |
| 1” | 5 | 3 | 3 |
| 1 1/4” | 6 | 4 | 4 |
| 1 1/2” | 8 | 4 | 5 |
| 2” 10 | 5 | 6 |  |
| 2 1/2” | 12 | 5 | 6 |
| 3” | 15 | 6 | 8 |
| 4” | 20 | 6 | 10 |

Welding temperature = 260( C or 500( F

C. Non-Contact Butt-Fusion

All pipe, valves, and fittings are to be prepared using the Radiant Heat

Butt-Fusion technique as outlined in ASTM D-2657 and according to the Asahi/America operation methods for non-contact butt-fusion methods.

Proper equipment selection should be based on installation requirements

and line sizes.

All basic Non-Contact Butt-Fusion equipment shall possess a minimum of the following capabilities:

1.  Computer Control of the welding process.

2.  Ability to store welding data internally on computer memory up to

1000 welds.

3.  Full alignment capabilities (vertical and horizontal).

4.  All metal components coated to prevent any particle generation from

metals.

5.  Ability to download all welding information to a personal computer.

Non-Contact Butt-Fusion equipment shall also have the following options incorporated into the tool for special demands:

1.  Protective hood over welding area.

2.  Nitrogen Purge of the welding area.

3.  Automatic Nitrogen purge of the pipeline.

4.  Security Card Entry.

5.  Printer Labels for each weld automatically.

Asahi/America offers the following Non-Contact butt-fusion tools for purchase

or rental.

The UF2000/1 - for sizes 1/2” - 2”

The UF2000/2 - for sizes 2 1/2” - 6”    (8” and 10” optional)

D.  Reduced Bead Butt-Fusion (Tekweld)

All pipe, valves, and fittings shall be prepared using a reduced bead method known as the Tekweld Method.  The Tekweld method is a butt-fusion process done according to ASTM D-2657 with additional parts to reduced the internal bead size.  Proper equipment selection should be based on line size.  For assistance contact Asahi/America.  The following Reduced Bead Tekweld tools are available from Asahi/America.

Tekweld 2 - for sizes 1/2” - 2”

Tekweld 6 - for sizes 1 1/2” - 6”

The UF2000/1 - for sizes 1/2” - 2”

The UF2000/2 Basic - for sizes 2 1/2” - 6”    (8” and 10” optional)

The UF2000/2 - for sizes 2 1/2” - 6”   (8” and 10” optional)

E. Beadless Fusion HPF

All pipe, valves and fittings 1/2" through 2" shall be performed using a beadless fusion method.  All welds are to be accomplished utilizing an external HPF coupling.

Each weld can be done utilizing an internal balloon for a complete bead and seam free weld.

Welds can also be done without utilizing a balloon, producing a beadless weld only.

All welds must be done utilizing pipe made of Solef 100 resin and fittings made of Solef 1009 resin.  All weld parameters are to be set utilizing the bar code scanner or reader.

4.  Suggested Work Facilities and Tools Facility

Subassembly and fabrication work should be conducted in a separate, temporary cleanroom located within the building Cleanroom should be equipped with the following to provide a clean installation:

A.  Provide Laminar flow Hepa filters in room ceiling to reach level of class 10,000 or better.

B.  The quantity of filters should be determined by providing a minimum of 60 room air changes per hour.

C.  Ideal setup is to place welding equipment directly under a filter.

In addition, nitrogen should be available for purging the pipelines with a positive pressure if the assemblies expand beyond the bounds of the room.  If utilizing the UF2000 tool, nitrogen purging can be controlled automatically by the welding device.

Tools

All fusion tools utilized and necessary miscellaneous tools are to be dedicated for clean build only, and should be kept separate.  Special attention should be given to the fusion tools to prevent the possibility of contaminating a weld.

To properly cut pipe without particle generation.  Proweld pipe cutters are recommended to cut up to 6” pipe nominal size.

The contractor shall lease or purchase all necessary welding equipment from Asahi/America.  At the end of the installation, any necessary equipment needed onsite should be sold to the owner.  Contractor is responsible for proper maintenance and care of the fusion tools during construction.  In the event of any unusual equipment malfunction.  Asahi/America is to be notified prior to any repair.

5.  Testing Procedures

Prior to pressure testing, the system shall be examined for the following items:

A.  Pipe shall be completed per drawing layout with all pipe and valve supports in place.

B.  Pipe, valves, and equipment shall be supported as specified, without any concentrated loads on system.

C.  Pipe shall be in good conditions, void of any cracks, scratches, or deformation.

a.  Pipe flanges shall be properly aligned.  All flange bolts should be 		     checked for correct torques.

b.  All joints should be reviewed for appropriate welding technique.

1.  Butt - To have two beads, 360( around the joint.

2.  Socket - To have two beads on the end of the fitting and on the

outside of the pipe in contact, 360( around the joint.

3.  UF2000 - Identify labels shall identify weld certification by the

print “welding OK”.   Joints should have  two beads 360( around 	               	               the joint.   Also refer to manufacturers separate weld inspection

criteria, supplied separately by Asahi/America.

If any deficiencies appear, the quality control engineer shall provide directions/repair.

Pressure Test

1.  Test fluid should be deionized water, with quality level set by Quality 		     Control Engineer.  In all cases test must be done hydrostatically.  Air is    	     not acceptable.

2.  Filling the system:  Open the valves and vents to purge the system of 	    	     air.

Slowly inject the water into the system, making sure that air does not 	  	     become trapped in the system.

3.  Begin pressurizing the system in increments of 10 PSI.  Bring the 	   	     system up to 100 PSI and hold.  Allow system to hold pressure for a 		     minimum of two hours and up to a recommended 12 hours.  Check 		     pressure gauge after one hour.  Due to natural creep effects in plastic	 	     piping, the pressure will have decreased.  If drop is less than 10% 		     pump the pressure back up.  At this time, the system may be fully 		     pressurized to desired test pressure.

4.  If after one hour the pressure has decreased more than 10%, consider

the test a failure.  Note the 10% value may need to be greater for 		     larger systems.  Also note that Step 3 may need to be conducted

several times if there are significant thermal changes.

5.  Test is to be witnessed by Quality Control Engineer, and certified by 		      the contractor.

6.  Obvious leaks can be found by emptying the system and placing a

10 PSI charge of clean, dry nitrogen on the system.  Each joint should 	      	     then be individually checked using a soapy water solution or an  		     Ultrasonic leak detection gun.  Leak detection guns should be 		  	     available from the pipe manufacturer.

Static Leachout Test According to Japanese Standard

(Temperature: 20(C; Performed once a year)

| Leach Out Quantity |
| --- |
| Analyzed Elements | Period (day) | PP-Natural | PVC (ug/m(,day) | PVDF (ug/m(,day) | Peek (ug/m(,day) | PP-Gray (ug/m(,day) |
| TOC | 1 7 30 | 200 120 73 | 600 270 82 | 66 40 26 | <69 <12 34 | 71 23 20 |
| Silica | 1 7 30 | <19.0 <3.0 <0.8 | <20 <3 <0.8 | <20 <3 <0.9 | <21 <3 <0.9 | <19 <3 <0.8 |
| Na | 1 7 30 | 1.90 0.96 0.15 | 32 0.34 0.27 | <0.30 <0.05 <.01 | 1.3 .013 .05 | 2.4 1.1 0.11 |
| K | 1 7 30 | <0.65 0.30 <0.03 | <0.70 <.10 <.03 | <.70 <.10 <.03 | <.70 <.10 <.03 | <0.65 <0.11 <0.03 |
| Ca | 1 7 30 | <1.3 0.41 0.07 | 240 35 3.0 | 1.3 .35 <.06 | <7 <1 <.3 | 2.9 0.41 <0.06 |
| Fe | 1 7 30 | <1.30 0.22 <0.06 | <1.3 0.30 0.45 | <1.3 <0.2 .07 | <1.4 <.2 <.06 | <1.3 <0.22 <.06 |
| Mg | 1 7 30 | <0.65 <0.11 <0.03 | 1.40 0.10 <0.03 | <0.7 <0.1 <0.03 | <0.7 <0.1 <0.03 | 5.1 0.70 0.38 |
| Sn | 1 7 30 | <9.70 <1.60 <0.42 | <10 <2 <0.4 | <10 <2 <0.4 | <10 <2 <0.4 | <9.7 <1.6 <0.42 |
| F | 1 7 30 | <6.5 2.8 4.5 | <7 <1 <0.3 | 120 71 65 | <7 <1 <0.3 | <6.5 <1.1 <0.3 |
| Cr | 1 7 30 | <6.5 <1.10 <0.28 | 20 7.0 4.7 | <7 <1 <0.3 | <7 <1 <0.3 | <6.5 <1.1 <0.28 |
| So4 2- | 1 7 30 | <6.50 <1.10 <0.28 | --- --- --- | --- --- --- | --- --- --- | 84 24 1.4 |

Static Leach Out Test According for Piping Nomura Micro Science Co., LTD

(Temperature: 80(C; Performed once a year)

|  |  |  | Leach Out | Quantity |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Analyzed Items | Period (day) | PP-Natural ((g/m2,day) | E-CTFE ((g/m2,day) | PVDF ((g/m2,day) | Peek ((g/m2,day) | PP-Gray ((g/m2,day) |
| TOC | 1 7 30 | 32000 11000 3600 | 15000 9800 1600 | 6500 3400 1600 | 630 51 19 | 7100 2800 1200 |
| Silica | 1 7 30 | <19.0 <3.0 <0.8 | <20 <3 <0.9 | <20 <3 <0.9 | <21 <3 <0.9 | <19 <3 <0.8 |
| Na | 1 7 30 | 1.90 0.96 0.15 | 32 0.34 0.27 | <0.30 <0.05 <.01 | 1.3 .013 .05 | 2.4 1.1 0.11 |
| K | 1 7 30 | <0.65 0.11 <0.03 | <0.66 <0.11 <0.03 | 1.5 0.12 <0.03 | 1.4 <0.1 <0.03 | 0.90 <0.11 <0.03 |
| Ca | 1 7 30 | <1.3 0.41 0.07 | 240 35 3.0 | 1.3 .35 <.06 | <7 <1 <.3 | 2.9 0.41 <0.06 |
| Fe | 1 7 30 | <1.30 0.22 <0.06 | <1.3 0.30 0.45 | <1.3 <0.2 .07 | <1.4 <.2 <.06 | <1.3 <0.22 <.06 |
| Mg | 1 7 30 | <0.65 <0.11 <0.03 | 1.40 0.10 <0.03 | <0.7 <0.1 <0.03 | <0.7 <0.1 <0.03 | 5.1 0.70 0.38 |
| Sn | 1 7 30 | <9.70 <1.60 <0.42 | <10 <2 <0.4 | <10 <2 <0.4 | <10 <2 <0.4 | <9.7 <1.6 <0.42 |
| F | 1 7 30 | <6.5 2.8 4.5 | <7 <1 <0.3 | 120 71 65 | <7 <1 <0.3 | <6.5 <1.1 <0.3 |
| Cr | 1 7 30 | <6.5 <1.10 <0.28 | 20 7.0 4.7 | <7 <1 <0.3 | <7 <1 <0.3 | <6.5 <1.1 <0.28 |
| So42- | 1 7 30 | <6.50 <1.10 <0.28 | --- --- --- | --- --- --- | --- --- --- | 84 24 1.4 |